## Min test std.requirement (V10)
Minimum Standard Testing requirement (Unit) of each country | [23 empty] | Issued | QA Planning (11 July 18)
R
Nisit / QA.Planning (Version.1)
|  |  |  | Relate country / Marks | [17 empty] | Issued | QA.Planning (13-Mar-24)
|  |  |  | Thailand | USA/Canada | Malaysia | Indonesia | Europe (PED) | UAE | Japan | Russia | France (NF-414) |  |  | India (QCO) |  |  | China |  |  | Singapore | Siripannee.N, Supatra.P / QA.Planning (Version 10)
[13 empty] | Philippines | [5 empty] | Taiwan | Hongkong
Europe (Keymark)
No. | Item test | Specification | type
1 | Pressure test | Refrigerant-containing part of an Air Conditioner must be performed. - Hi side (R410A) --> 4.15 Mpa.(601 psig or 42 kgf/cm2) (R32) --> 4.17 Mpa.(605 psig or 42.5 kgf/cm2) - Low side --> 2.21 Mpa (320 psig) | R | - |  | - | - |  | - | - | - | - | - |  | - |  | - | -
|  | Compress Air or Nitrogen hold 1 min. as below Cooler - R22 and R407C ³ 1.570 Mpa. - R410A ³ 2.490 Mpa. - R32 or others ≥1.25 x operating pressure Condenser - R22 and R407C ³ 2.415 Mpa. - R410A ³ 3.865 Mpa. - R32 or others ≥1.25 x operating pressure | R |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
2 | Insulation test | 500VDC 1 sec. (Insulation ³ 10MW) (Refer to MCP spec.) | R |  | - | - | - | - | - | - |  |  | - | - | - | - | - | -
|  | 500VDC 1 sec. (Insulation ³ 1 MW) | R | - | - | - | - | - | - | - | - | - | - | - | - | Cancel in Amd 1 | - | -
3 | Power input & Current | During normal operating by T1 or T3 condition (Depend on specified by manufacturer) - >25W.and ≤ 300W.(The diviation ≤ 20%) - > 300W. (The diviation ≤ 15% or 60W.) Current Judgement - >0.2A and ≤ 1.5A (The diviation ≤ 20%) - > 1.5A (The diviation ≤ 15% or 0.3A.) | R |  | - | - | - | - | - | - | - | - | - | - | - |  | -
|  | The outdoor unit of the air conditioner/heat pump [connected with dummy indoor unit (IDU)] shall be run at the rated voltage and the power shall be measured. The measured power input shall meet the limits prescribed by the manufacturers when tested at the prevailing ambient conditions during the manufacturing process. | R | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
|  | During normal operating by T1 or T3 condition (Depend on specified by manufacturer) Input Judgement - >25W.and ≤ 300W.(The diviation ≤ 20%) - > 300W. (The diviation ≤ 15% or 60W.) Current Judgement - >0.2A and ≤ 1.5A (The diviation ≤ 20%) - > 1.5A (The diviation ≤ 15% or 0.3A.) Remark : Measurement need to separate between indoor and outdoor. | S | - | - | - | - | - | - | - | - | - |  | - | - | - | - | -
4 | Electric strength test (Hi pot) | Testing voltage will be performed and hold 1 sec as below Indoor unit - Terminal - Box --> Supply 2500VAC or - Terminal - Metal parts --> Supply 1000VAC Outdoor unit - Terminal - Metal parts --> Supply voltage 1000VAC 1 sec. No breakdown shall occur !!!( Leak current £ 5mA and maximum £ 30mA.) **India model : - IS1391-2 Amd.4 INV unit's compressor drive, earthingwire from accessible metal part may be remove before testing - IS:8148 Amd.1 : approximately 50Hz for 1s. For inverter unit or units with surge protection,remove the earthing wire of the inverter drive/surge protection device before testing, as Variable Frequency Drives (VFDs) provide a ground path for noise (electrical) filter. | R |  | - |  |  |  |  | - | [6 empty] | -
|  | For Class I appliances, the insulation of the appliance shall be subjected to a voltage of substantially sinusoidal waveform having a frequency of approximately 50 Hz or 60 Hz for 1 s. The value of the test voltage shall be two times rated voltage plus 1 000 V. No breakdown shall occur !!! ( Leak current ≤ 5mA and maximum ≤ 30mA.) | R | - |  | - | - | - | - |  | - | - | - | - | - | - | - | -
|  | Testing voltage will be performed and hold 1 min as below table. No breakdown !!! shall occur during the test. (Once in a year for each function and rating) ** CCC : setting, 60Sec, not breakdown Supply voltage --> Cl.13/Cl.16 - L,N and Earthed metal parts : 1000V/1250V - Parts separated by supplementary insulation : 1750 V/1750V - L,N and Accessible Non-metallic part : 3000V/3000V | S | - | - | - | - | - | - | - | - | - |  | - |  |  | - | **
5 | Earth Continuity | Supply current > 10A.from a source having a no-load voltage not exceeding 12V.then the Insulation resistance ≤ 0.1Ω | R |  | - |  |  |  | - | [5 empty] | - | - | -
|  | Supply current >=25 A .then the Insulation resistance ≤ 0.1Ω | S | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | **
|  | Supply current from a source having a no-load voltage not exceeding 12V.(ac ord dc) and equal to 1.5 times rated current of appliance or ≥ 25 A.is passed between earth terminal or earthing contact and each of accessible metal parts in turn then the Insulation resistance ≤ 0.1Ω | R | - | - | - | - | - | - | - | - | - | - | - |  |  | - | -
|  |  | S | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
6 | Functional test / Running test | The correct functioning of an appliance is checked by inspection or by appropriate test if the incorrect connection or adjustment of components has safetly implications. | R | - | [10 empty] | - | - | - | -
|  | Outdoor unit of the air conditioner / heat pump shall be run (by connecting with dummy indoor unit of run test facility after the final assembly) at the rated voltage and measure the power. The measured power meets the limit set by the quality assurance with respect to prevalent ambient temperature. Indoor unit (to be tested after the final assembly) of the air conditioner / heat pump and shall be run alone to check the proper running of blower. | R | - | - | - | - | - | - | - | - | - | - | - |  |  | - | -
|  | Split unit — Indoor unit (IDU) and outdoor units (ODU) shall be run separately (without connecting IDU and ODU) to check the fan/blower running only. Compressor need not to be run during this test. | R | - | - | - | - | - | - | - | - | - | - | - | - | Cancel in Amd 1 | - | -
7 | Leak current | *** This items will be perfomed after Heating test. --> Air Cond.is operated under most severse condition and Supply voltage between live parts (L-N) 106% of rate VAC which is identified on name plate then the leak current ≤ 2 mA./kw.input with a maximum value of 10 mA.for appliance accessible to the general public, and maximum value of 30 mA.for appliances not accessible to the general public. *** If calculate the leakage current, the result is lower than 3.5 mA. then identify the result is 3.5 mA. | R | - | - | - | - | - | - | - | - | - | - | - |  | Cancel in Amd 1
|  |  | S | - | - | - | - | - | - | - | - | - |  | - |  |  | - | **
8 | Critical component check | ** Require only sampling test** | S | - |  |  |  | - | - | - |  | - | - | - | - | - | - | -
9 | Brazing quolification & Monitored | All operators working on all permanent assemblies must be quolified. | R | - | - | - | - |  | - | - |  |  | - | - | - | - | - | -
10 | Leakage test | The manufacturer shall carry out a leak test of the refrigeration circuit at the operating pressure. | R | - | - | - | - | - |  | - | - |  | - |  | - | - | - | -
|  | Indoor unit : leak test after refrigerant/gas charging to ensure that there is no leakage in the refrigerant circuit using a leak detector. Outdoor : with or without panel fitted on it, shall be subjected to leak test after refrigerant charging to ensure that there is no leakage in the refrigerant circuit using a refrigerant leak detector. | R | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
|  | Each Heat Ex.coil will be performed Helium leakage test as following. 1. The coil is pressurized the helium gas. The tracer gas concentration should be 20% by volume. 2. The coil should be pressurized to as minimum of 0.42 Mpa (60 PSI) or Max.allowable design pressure. 3.The tip of probe should be within 5 mm., Normally a snipper probe speed of around 4 cm/sec. or less is adequate 4. The leak rate of helium gas ≤ 2.51x10-5 mbar l/s. (Reference from IS11329 Amd.2) | R | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
11 | Vacuum pressure | < 0.1 bar | R | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
| 5.25 Vaccuum test | a) Achieve vacuum 300 micron using vacuum pump for outdoor unit to control moisture content in refrigerant circuit; b) Before refrigerant charging vacuum level should not be more than 300 microns in maximum 15 s; c) This test shall be carried out during the manufacturing process of the outdoor units.’ | R | - | - | - | - | - | - | - | - | - | - | - | -
12 | Visual test | All of components and marking must follow to DWG.and std.of each country. | R | - | - | - | - | - |  |  |  | - | - | - | - | - | - | -
|  | The visual inspection to be carried out for any abnormal scratches, dents as defined in quality management system. The ends will be covered with caps, plugs or polythene wrapping to prevent any contamination entering in heat exchangers, if stored for more than 72 hr. (3 days) | R | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
13 | Availabe of spare parts | Manufacturer must guarantee the availability of spare parts for 10 years after the product is taken off the market. | R | - | - | - | - | - | - | - |  |  | - | - | - | - | - | -
14 | Marking | Rubbering this mark by hand 15s then cloth soaked with water 15s.and cloth soaked with petroleu spirit. Judgement : the marking shall be clearly legible. It shall not be easily possible to remove marking paltes nor shall they show curling | S | - | - | - | - | - | - | - | - | - |  | - | - | - | - | **
15 | Protection against access to live parts | Remove all detachable part 1. Through openings --> Test probe B of IEC 61032 is applied without appreciable force (≤1N.), through openings all directions. If it can't entry, the force on the probe in the straight position is increased to 20 N. 2. Class II construction, If any --> Use Test probe 13 of IEC61032 is applied without appreciable force (≤ 1N.) through opening by all directions. Judegement : Probe must not access to live parts. (Once in a year for each function and rating) | S | - | - | - | - | - | - | - | - | - |  | - |  |  | - | **
16 | Heating | During normal operating by T1 or T3 condition (Depend on specified by manufacturer or most serve condition) --> Operated in the cooling / heating mode continuously until to steady conditions by supply voltage between 0.94 times the lowest rated voltage and 1.06 times the highest rated voltage. Judgement : 1. Shall not exceed the values shown in Table 3 of IEC 60335-2-40 & IEC 60335-1. 2. Protective devices shall not operate and sealing compound shall not flow out. 3. Temp.of the air in the outlet duct shall not exceed 90oC | S | - | - | - | - | - | - | - | - | - |  | - | - | - | - | **
17 | Abonormal operation | ** Ambient temp.will be set 23±5oC 1). Motor locked --> Operated for 15 days (360 hr) or until a protection device permanently if the temp.of the motor windings doesn't exceed 90oC when steady conditions are established, the test is considered to be ended. Judgement : During the test, the temp.of the enclosure shall not exceed 150oC and temp.windings shall not exceed the values as below table. However, At the end of test, the leakage current between the windings and the enclosure is measured and shall not exceed 2 mA, the motor being supplied at twice the rated voltage. | S | - | - | - | - | - | - | - | - | - |  | - | - | - | - | **
2). Comp.locked --> If Comp.has IEC 60335-2-34 Cert. then no need to test. 3). Air Cond.incorporating 3 phases motors. -->Operated under the most serve conditions and Supplied at rated voltage or at the upper limit of the rated voltage range with one phase disconnected. Operated until to steady conditions are obtained or the protective device operates. 3. After the tests, the insulation when it has cooled down to approximately room temp., shall withstand the Electric strength test. 4). Restricted or shut off --> Operated under the conditions in Clause 11 (Heating) and supplied at rated voltage or at the upper limit of the rated voltage range. (Ambient temp. of 23±5oC) then close outdoor heat whichever is the most unfavourable without nonoperative and repeat again at indoor heat like as outdoor unit.
17 | Abonormal operation (Continue) | 5). Air to Air appliance --> Operated Air cond.by supply rate voltage or upper limit of rate voltage under the conditions specified in Clause 11 (Heating) then reduce dry-bulb temp. 5K.below than minimum value specified by manufacturer (If heat mode). However, the test is repeated except except that dry-bulb temp.is increased to a value 10K above the max temp.specified by manufacturer. (if cooling mode) Judgement : 1. Not emit flames or molten, or poisonous or ignitable gas in hazardous amounts. 2. Enclosure shall not deform and temp.shall not exceed the values as below table. 6). Defect that may be expected during normal use --> Operated under condition in Clause 11 and at rat voltage then apply normal fault conditon may happen during normal use. 7). For all circuits or parts of circuits --> 7.1 Short circuit of functional insulation if clearances or creepage distances are less than the values specified in clause 29. 7.2 Open circuit at the terminals of any component. 7.3 Short circuit of capacitors in case of they didn't comply with IEC60384-14 | S | - | - | - | - | - | - | - | - | - |  | - | - | - | - | **
7.4 Short circuit of any two terminals of electronic. other than an integrated circuit.(Except optocoupler) 7.5 Failure of triacs in the diode mode. 7.6 Failure of an integrated circuit (Microprocessors) all possible output signals. 7.7 Failure of an electronic power switching device in a patrial tun-on mode with loss of gate (base) control. 7.8 For any of the faulty conditions specified in 19.11.2, the safety of the appliance depends on the operation of miniature fuse-link complying with IEC 60127, the test is repeated but withminiature fuse-link replaced by an ammeter.
18 | Stability and mechanical hazards | Use Test probe B of IEC 61032 with circular 50 mm. by apply a force not exceeding 5 N. Judgement : It shall not be possible to touch dangerous moving parts with this test probe. | S | - | - | - | - | - | - | - | - | - |  | - | - | - | - | -
19 | Mechanical strength | 1. Spring hammer --> Apply 3 blows which having an impact energy of 0.5J in every point (protect live part) likely to weak. Judgement : After test, No damage and compliance with clause 8.1 (protection against to live parts), 15.1 Moisture resistance and 29 (Clearance) shall not be impaired. 2. Pressure test --> Filled a liquid to hydraulic pump and apply the pressure at least 3 times the maximum design pressure (hold 1 min) during operate under Heating and abnormal test. Judgement : No leakage happeing. | S | - | - | - | - | - | - | - | - | - |  | - | - | - | - | -
20 | 9.9 Cooling Capacity test | Testing will be performed at Std.Condition (DB/WB) -> (In 27/19 Out 35/- then determine as following function 20.1 Total cooling effect 20.2 Total dehumidifying effect 20.3 Total sensible cooling effect 20.4 Total air capacity for cooling * The test shall be run 1 hr.recording data every 10 min, giving 7 sets for reading. Judgement : Capacity test of production unit ≤ 95% of name plate rating. (Once in two years for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
21 | 9.11 Measurement of ISEER | The test condition for measurement of ISEER for cooling shall be as specified in Cooling capacity test. The method of calculation and the bin temperature distribution shall be as given in Annex J. The ISEER of the production unit shall be not less than 95% of the name plate rating. Capacity and power at half load shall be within ±5 percent of the rated half load capacity (Once in a year for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
22 | Capacity rating test | Testing must be done Cooling and Heating capaicty with extension pipe 5-7.5 m.at std.condition. (Unit running 1 hr.and record 7 sets) | S | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
23 | 8.3 Maximum cooling conditions test | Testing will be performed at Std.Condition (DB/WB) -> (In 35/24 Out 46/27). 1.The air cond.motors should operate continuously for the first 1 hr.of the test without tripping of the motor overload protective device. 2.Motor overload protective device may trip only during the first 5 min after the shut-down period of 3 min. 3. Resumption of operation doesn't occur after initial trip within the first 5 min. | S | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
24 | 12.3.1 Room discharge air flow rating test (Annex C) | It will be performed at Cooling std.condition(DB/WB) -> (In 27/19 Out 35/24) with the controls set for maximum cooling and with the fresh air and exhaust dampers, if any, properly closed. (Once in two years for each type and rating) | S | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
25 | 9.3 Power factor test | Operating under full load capacity under std.condition test. with controls set for maximum cooling and with ventilating air damper and exhaust damper, if any, closed, the split air conditioner shall have overall power factor, measured at rated voltage and frequency ≥ 0.9 (Once in 2 years for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
26 | 9.4 Maximum operating conditions test | Test will be conducted at Max operating conditions and Heating overload then this test is to prove that capable of operating satisfactorily then During one entire test, should operate without visible or audible indication of damage and without tripping (Once in two years for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
27 | 9.5 Freeze up test | The air blockage test and the drip test shall be conducted under Freeze-up conditions (DB/WB) -> (In 21/15 Out 21/-) at 85% and 115% of rated voltage then During the test no ice shall drop from the units and no water shall drip or blow off the unit. (Once in 2 years for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
|  | The air blockage test and the drip test shall be conducted under Freeze-up conditions (DB/WB) -> (In 21/15 Out 21/-) at rated voltage then During the test no ice shall drop from the units and no water shall drip or blow off the unit. (Once in a year or whenever there is a change in design, whichever is earlier. ) | S | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
28 | 9.5.3 Air blockage test | Test should be continuous, with the unit on the cooling cycle for 4 hr.after establishment of the specified temp.conditions. At the end of 4 hr.of operation, any accumulation of ice or frost on the evaporator shall not cover more than 50% of the indoor side face area of the evaporator coil. (Once in 2 years for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
29 | 9.5.4 Drip test | The units should be operated for 4 hr.with completely block air inlet of evaporator coil then after 4 hr., the unit shall be stopped and air-inlet covering removed until the accumlation of ice or frost has melted. The unit shall then be turned on again with fan operating at the highest speed for 5 min then During the test no ice shall drop from the unit and no water drip or blow off (Once in 2 years for each function and rating) (*IS8148: Once in a year or whenever there is a change in design, whichever is earlier) | S | - | - | - | - | - | - | - | - | - | - | - |  |  | - | -
30 | 9.6/8.6 Enclosure sweat test | The test will be conducted at (DB/WB) -> (In 27/24 Out 27/-) then During the test, no condensed water shall drip, run of blow off the unit. (Once in 2 years for each function and rating) (*IS8148: Once in a year or whenever there is a change in design, whichever is earlier) | S | - | - | - | - | - | - | - | - | - | - | - |  |  | - | -
31 | 9.7 & 9.8 /8.8 Power consumption test | 26.1 The Cooling test will be conducted at (DB/WB) -> (In 27/19 Out 35/24) then During the test shall not exceed 110% 26.2 The Heating test will be conducted at (DB/WB) -> (In 20/- Out 7/6) then During the test, the power shall not exceed 115% of the rated energy for heating. (Once in 2 years for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
|  | 26.1 The Cooling test will be conducted at (DB/WB) -> (In 27/19 Out 35/-) and the Heating test will be conducted at (DB/WB) -> (In 20/- Out 7/6) then the power consumption shall be the average during the capacity rating test. (Once in two years for each rating) | S | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
32 | 9.9 Cooling Capacity test | A.) Up to 10 500 W — For each unit tested, the following tolerances shall be applicable: - The measured standard cooling at full capacity shall not be less than 95 percent of the rated value; and - The measured standard cooling at 50 percent of full capacity shall be ± 5 percent of full load capacity. B.) Above 10 500 W up to and including 18 000 W — For each unit tested, the following tolerances shall be applicable: - The measured standard cooling at full capacity shall not be less than 90 percent of the rated value; and - The measured standard cooling at 50 per cent of full capacity shall not vary by more than ± 5 percent of full capacity. (Once in 2 years for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
33 | 9.10 Heating Capacity Test | The measured standard heating capacity at full capacity shall not be less than 90 percent of the rated value. (Once in 2 years for each function and rating) noted : more detail please as IS1391-2 : 2023 Cl.9.10 | S
34 | 9.13 / 11 Sound test | Operate in Cooling mode and noise must not over than below table. *Background noise should be less than the measured value 11 dBA (Once in two years for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
|  | Test condition In/Out (27±5oC and 35±5oC) then take average of 3 reading to arrive at sound pressure. *Background noise minimum 10 dB lower than rated sound pressure level or 20 dB whichever is higher. (Once in two years for each type) | S | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
35 | 9.11 Heat Pump Heating Capacity Test | For all heating capacity tests, the requirements specified in Annex E shall apply. Testing shall be conducted using the Calorimeter test method (see Annex G) or Indoor Air Enthalpy test method (see Annex H). The measured heating capacity shall not be less than 90% of the rated heat pump capacity. (Once in two years for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  | - | - | -
35 | 9.1 Heating Capacity Test | Testing will be performed at Std.Condition (DB/WB) -> (In 20/15 Out 7/6). The electrical energy supplied to the heat pump during the test shall be recorded, at the termination of each defrost cycle during the data collection period. (Once in two years for each type and rating) | S | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
36 | 9.12 / 9.2 Maximum Heating Performance Test | Testing will be performed at Std.Condition (DB/WB) -> (In 27/- Out 24/18) and test voltage at 90% of lower rate voltage and 110% of rate higher rate voltage then During the testing have no any indication of damage. The equipment shall be permitted to stop and start under the control of an automatic limit device, if provided. After the interruption of operation, the equipment shall resume operation within 30 min. (Once in two years for each function and rating) | S | - | - | - | - | - | - | - | - | - | - | - |  |  | - | -
37 | 9.3 Automatic Defrost Performance Test | Testing will be performed at Std.Condition (DB/WB) -> (In 20/15 Out 2/1). During the defrost period, the temperature of the air from the indoor-side of the equipment shall not be lower than 18oC for longer than 1 min. (Once in two years for each type and rating) | S | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
38 | 8.7 Condensate Disposal test | The test will be conducted at (DB/WB) -> (In 27/24 Out 27/-) with 4 hr.operating at rate voltage and rate freq. The unit’s controls, fans, dampers and grillers shall be set to produce the maximum tendency to sweat, provided such settings are not contrary to manufacturer’s operating instructions then During this test, the air conditioner shall have the ability to dispose of all condensate and there shall be no dripping or blowing off of water from the unit such that the building or surroundings may become wet. (Once in two years for each rating) | S | - | - | - | - | - | - | - | - | - | - | - | - |  | - | -
39 | Provision for earthing | 27.1 Accessible metal parts of class 0I and I appliances shall be permanently and reliably connected an earthing terminal within the appliance and Earthing terminals and earthing contacts shall not be connected to the neutral terminal. 27.2 The clamping means of earthing terminals shall be adequately secured against accidental loosening. 27.4.1 Parts providing earthing continuity, other than parts of a metal frame or enclosure, shall be of metal having adequate resistance to corrosion. 27.4.2 If these parts are of steel, they shall be provided with an electroplated coating have a thickness of at least 5 mm. 27.4.3 Parts of coated or uncoated steel that are only intended to provide or to transmit contact pressure shall be adequately protected against rusting. 27.5 The connection between the earthing terminal or earthing contact and earthed metal parts shall have low resistance which is checked by Supply current from a source having a no-load voltage not exceeding 12V.(ac ord dc) and equal to 1.5 times rated current of appliance or ≥ 25 A.is passed between earth terminal or earthing contact and each of accessible metal parts in turn then the Insulation resistance ≤ 0.1Ω | S (1391) R (8148) | - | - | - | - | - | - | - | - | - | - | - |  |  | - | -
40 | 7.1.1 Internal Contamination | Total residue contamnation is maximum 100 mg/m2 of total internal surface area of which 40 mg/m2 max may be soluble and 60 mg/m2 max my be insoluble. (Once in a week) | S | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
41 | 7.3 Test for Mechanical Strength | Testing will be performed as following items. 40.1 Burst test --> 2 samples of each type of component are to be tested 40.1.1 Withstand 3 times of design pressure on low pressure side 40.1.2 Withstand 5 times of design pressure on high pressure side 40.2 Fatigue test --> 1 sample of each type of component are to be tested. This is the cyclic test consisting of 250,000 cycles as following. a) 1st cycle, the test samples are to be filled with water by hydraulic pump system. The pressure is to be raised graually until to the highest pressure (holding 1 min). b) 2nd to 250,000 cycle are the pressure within each sample shall be raised and lowered (holding at least 0.1 sec of each cyclic) c) Cycle test pressure - Heat Ex.at high side, the upper pressure values shall not be less than the staurated vapour presure of refirgerant at 49oC and the lower pressure value shall not be grater than the saturated vapour pressure of the refrigerant at 4.4oC. (Once in a year for each type) | S | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
42 | 7.4 Test for Corrosion Resistance | Heat Ex.material shall be corrosion resistant as following testing. 41.1 Type of Corrosion (Galvanic & General) 41.2 Type of Environment 41.3 Selection of Mat.base on Environemntal Condition. *** Salt spray test should be done at least 72 hr. (If the size of Heat Ex.is large and not able to fit into the salt spray chamber, then we can prepare small replica to test) | S | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
43 | 7.2 Leakage test | Each coil shall undergo leak test to conform tightness specification. 7.2.2 Helium leak test Helium is being used as tracer gas, sensitive to detect minute leaks in heat exchanger assemblies b) Sniffer Test Method 1) The coil is pressurized with helium gas. If required due to large volume, the tracer gas concentration should be 20 percent by volume; 2) Unless otherwise specified by the manufacturer, the coil should be pressurized to a minimum of 0.42 MPa (60 PSI) or maximum allowable design pressure; 3) The tip of the probe should be within 5 mm of the surface being scanned. Normally a snipper probe speed of around 4 cm/sec or less is adequate; and 4) The leak rate of helium gas from any surface shall not be more than 2.51x10 -5 mbar l/s | R | - | - | - | - | - | - | - | - | - | - | - | - | - |  | -
44 | Moisture resistance | - The enclosure of the appliance shall provide the degree of protection against moisture in appliance - Appliances subject to spillage of liquid in normal use shall be constructed so that such spillage does not affect their electrical insulation - Appliances shall be proof against humid conditions that may occur in normal use | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | **
|  |  |  | TIS1155-2557, TIS2134-2553 TIS1375, TIS1529 | ETL report of each model UL60335-1, UL60335-2-40 | MS IEC60335-1, MS 1597-2-40 | SNI 04-6292.1, SNI IEC 60335-2-40 | IEC60335-1, 60335-2-40, PED | ECAS, EQM, U.A.E. STANDARD NO.1005/2000 | Denan Law | EAC | NF414 V.15, NF EN50106 | DAO 18-03, PNS IEC 60335-2-40, PNS IEC 60335-1 | European Keymark Scheme for Heat Pumps (Annex B) | IS1391 & SIT 4-Aug-21 | IS8148-2018 & SIT 4-Aug-21 | IS11329 & PM 3rd Feb-21 | GB4706.1 & GB4706.32
Standard Specification for reference
Remark :
[5 empty] | Should be tested (If possible) | [5 empty] | Std.requirement which can select testing
[5 empty] | Std.requirement (Must be tested) | [5 empty] | (Between Pressure and Refri. leakage test.) --> QCO
Std.requirement must be tested at
external lab --> CCC
QAP022-012
V : Voluntary mark
M : Mandatory mark
S : Sampling test
R : Routine test
*
*
*
Revision :
Version 4 : Add requirement of Keymark std.
Version 5 : Add requirement of QCO (IS std.)
Version 6 : Review requirement of QCO to same new amendment.
Version 7 : Add requirement of CCC std.
Verison 8 : Review requirement of QCO to same new amendment.
Verison 9 : Update requirement QCO
Verison 10 : Review requirement of leak current and Electric strength test. moreover, reviewing requirement of QCO and CCC.
**

## Scope standard
Product Scope
Standard | Country | Scope
TIS 1155-2557 | Thailand | Room air conditioner split-type, air to air or air to water by water supply to condensing unit rate not over 100 L/h by using hermatic motor compressor, Alternating current, frequency 50 Hz, capacity up to 12,000 W.
TIS 2134-2565 | Thailand | Room air conditioner capacity up to 18,000 W with rated voltage being not more than 250 V for single-phase appliances and 480 V for other appliances.
TIS 1529-2561 | Thailand | Room air conditioner including motor-compressor, rated voltage being not more than 250 V for single-phase appliances and 480 V for other appliances. This standard is cover to air conditioner cooling capacity up to 18,000 W.
UL60335-1, UL60335-2-40 | USA | household and similar purposes, their RATED VOLTAGE being not more than 250 V for single-phase appliances and 480 V for other appliances.
MS IEC60335-1, MS 1597-2-40 | Malaysia | AIR CONDITIONER Cooling Capacity of 32,000 Btu/hr & below Split Air-conditioner, Portable Air-conditioner, Ceiling Air-conditioner
MS 2597:2014 |  | single-phase non-ducted single split wall mounted type vapour compression air conditioners with cooling capacity up to 7.1 kW.
SNI 04-6292.1, SNI IEC 60335-2-40 Permenperind No.34/M-IND/PER/7/2013 | Indonesia | Split air conditioner, Window and/or portable with cooling capacity up to 27,000 BTU/h or 7,913 W and rate voltage not morn than 250 V.
IEC60335-1, 60335-2-40, PED | Europe | pressure equipment and assemblies with a maximum allowable pressure PS greater than 0.5 bar
ECAS, EQM, U.A.E. STANDARD NO.1005/2000 | Middle East | will update again after training
NF414 V.15, NF EN50106 | France | ATW that sale in France (now we apply only AWHP 4.5 MRR0.TH model)
DAO 18-03, DAO 22-01, DAO 22-02 PNS IEC 60335-2-40, PNS IEC 60335-1 | Philippines | Inverter, non-inverter, window type and split-type (wall-mounted, floor-standing, cassette-type, and ceiling suspended) air-conditioners with maximum rated voltage not more than 250V for single phase and 600V for all other type and cooling capa up to 50,000 kJ/hr.
European Keymark Scheme for Heat Pumps (Annex B) | Europe | ATW that sale in Europe Except PUMY that can conect with many indoor not only ATW
IS 1391-2 : 2023 (non-duct type) | India | Single or three phase non-ducted split with single stage, two stage, multi-stage, fixed and variable speed air conditioner of rated capacity up to and including 18,000 W
IS 8148 : 2018 (duct type) | India | Split ducted air conditioners having air-cooled and water cooled condenser, and ducted air to air heat pumps Except Multi-split-system air-conditioners and air-to-air heat pumps (VRF)
IS 11329 : 2018 (heat exchanger) | India | heat exchangers used for the manufacturing of room air conditioners up to and including the capacity of 18,000 W. NOTE : The heat exchanger for air-conditioners other than IS 1391 (Part 1) and (Part 2) is under consideration.
IS 10617 : 2018 (compressor) | India | 1. Hermetic sealed type standalone motor-compressors operating on vapor compressor cycle, suitable for low, medium and high temperature applications based on reciprocating (including linear), rotary and scroll pump mechanisms, their protection system, if any, which are intended for use in equipment for house hold, industrial and commercial purposes. 2. Motor-compressors tested separately under the most severe conditions that may be expected to occur in normal use, their rated voltage being not more than 260 V for single-phase motor-compressors and not more than 480 V 3. Does not cover semi-hermetic compressor
GB4706.1 & GB4706.32 | China | Air conditioners cooling capacity shall not exceed 21,000 cal/h (24.4 kW) | http://www.china-ccc.org/scope-of-CCC

## Sheet1
Approved | issued
Siripannee.N Supatra.P